## Thermal
Approximate Voltage Class	Voltage Rating	phase	Type	Name	MVA	wound limb	return	Estimated GIC per Phase Per Unit E field (A/(V/km))	Estimated Fractional Population of the voltage and phase class	Assumed Fractional Population For this voltage class and phase	This transformer type fractional population	Asymptotic Temp rise at 100 A GIC ( design 2)	Asymptotic Temp rise at 200 A GIC (design 2)	Asymptotic Temp Rise per unit E field: slope ((degrees C)*(V/km)^-1)	Asymptotic Temp Rise per unit E field: offset (degrees C)	This transformer age 25-40 (25% of transformers, 160C short term limit) Fractional Population	This transformer age 0-25 (36% of transformers, 180C short term limit) Fractional Population	This transformer age >40 (39% of transformers, 140C short term limit) Fractional Population	height y axis (pixels)	Temp range y axis (K)	width x axis (pixels)	Time range x axis (seconds)	Height 100C to 200C (pixels)	63% of height (px)	pixels along x for 63% height	time constant (s)	time constant (m)
				name										alpha	beta	pop25to40	pop0to25	pop40plus								tau
500	526	single	GSU	Tie1	92	one	two flux return	37	0.107467406380028	0.142857142857143	0.015352486625718	150.4	167.2	6.21599999999999	133.6	0.00383812165643	0.005526895185259	0.00598746978403	289	180	599	21600	29	18.27	14	504.841402337229	8.41402337228715
500	525	single	Auto	Tie2	374	one	two flux return	37	0.107467406380028	0.142857142857143	0.015352486625718	152.4	187.3	12.913	117.5	0.00383812165643	0.005526895185259	0.00598746978403	289	200	599	21600	54	34.02	14	504.841402337229	8.41402337228715
500	525	single	Auto	Tie3	500	two	no return	37	0.107467406380028	0.142857142857143	0.015352486625718	140.1	175.8	13.209	104.4	0.00383812165643	0.005526895185259	0.00598746978403	289	200	599	21600	48	30.24	11	396.661101836394	6.6110183639399
500	525	three	Auto	Tie4	300	three	no return	37	0.055361997226075	0.25	0.013840499306519	171.6	220.5	18.093	122.7	0.00346012482663	0.004982579750347	0.005397794729542	289	250	599	21600	48	30.24	9	324.540901502504	5.40901502504174
500	525	three	Auto	Tie5	560	three	no return	37	0.055361997226075	0.25	0.013840499306519	172.3	238	24.309	106.6	0.00346012482663	0.004982579750347	0.005397794729542	289	250	599	21600	79	49.77	14	504.841402337229	8.41402337228715
500	500	single	Auto	Tie6	292	two	two flux return	37	0.107467406380028	0.142857142857143	0.015352486625718	141.5	168.2	9.879	114.8	0.00383812165643	0.005526895185259	0.00598746978403	289	180	599	21600	45	28.35	13	468.781302170284	7.81302170283806
500	500	single	Auto	Tie7	672	two	two flux return	37	0.107467406380028	0.142857142857143	0.015352486625718	120.9	153.7	12.136	88.1	0.00383812165643	0.005526895185259	0.00598746978403	289	180	599	21600	54	34.02	12	432.721202003339	7.21202003338898
500	525	single	Auto	Tie8	460	two	two flux return	37	0.107467406380028	0.142857142857143	0.015352486625718	133.2	167.1	12.543	99.3	0.00383812165643	0.005526895185259	0.00598746978403	289	180	599	21600	56	35.28	13	468.781302170284	7.81302170283806
500	500	three	Auto	Tie9	840	three	two flux return	37	0.055361997226075	0.25	0.013840499306519	157.8	193.7	13.283	121.9	0.00346012482663	0.004982579750347	0.005397794729542	289	250	599	21600	43	27.09	13	468.781302170284	7.81302170283806
500	525	three	GSU	Tie10	300	three	two flux return	37	0.055361997226075	0.25	0.013840499306519	142.2	161.4	7.10400000000001	123	0.00346012482663	0.004982579750347	0.005397794729542	289	180	599	21600	32	20.16	12	432.721202003339	7.21202003338898
735	735	single	GSU	Tie11	100	two	no return	34	0.015606102635229	0.333333333333333	0.005202034211743	153.9	174.6	7.038	133.2	0.001300508552936	0.001872732316227	0.00202879334258	315	200	645	21600	36	22.68	16	535.813953488372	8.93023255813954
735	765	single	Auto	Tie12	373.33	two	two flux return	34	0.015606102635229	0.333333333333333	0.005202034211743	160.5	194.8	11.662	126.2	0.001300508552936	0.001872732316227	0.00202879334258	315	250	645	21600	47	29.61	15	502.325581395349	8.37209302325581
735	746	single	Auto	Tie13	750	two	two flux return	34	0.015606102635229	0.333333333333333	0.005202034211743	142.9	179.6	12.478	106.2	0.001300508552936	0.001872732316227	0.00202879334258	315	200	645	21600	62	39.06	16	535.813953488372	8.93023255813954
345	400	single	Auto	Tie14	167	one	two flux return	9	0.065409153952843	0.142857142857143	0.009344164850406	134.2	154.9	1.863	113.5	0.002336041212602	0.003363899346146	0.003644224291658	289	180	599	21600	36	22.68	15	540.901502504174	9.01502504173623
345	420	single	Auto	Tie15	360	one	two flux return	9	0.065409153952843	0.142857142857143	0.009344164850406	135.5	163.4	2.511	107.6	0.002336041212602	0.003363899346146	0.003644224291658	289	180	599	21600	47	29.61	13	468.781302170284	7.81302170283806
500	433	single	GSU	Tie16	121.33	two	no return	37	0.107467406380028	0.142857142857143	0.015352486625718	127.8	150.4	8.362	105.2	0.00383812165643	0.005526895185259	0.00598746978403	289	160	599	21600	43	27.09	13	468.781302170284	7.81302170283806
345	410	single	GSU	Tie17	94	two	no return	9	0.065409153952843	0.142857142857143	0.009344164850406	128.4	146.8	1.656	110	0.002336041212602	0.003363899346146	0.003644224291658	289	160	599	21600	36	22.68	14	504.841402337229	8.41402337228715
345	420	three	Auto	Tie18	750	three	no return	9	0.370651872399445	0.111111111111111	0.041183541377716	116.8	154.1	3.357	79.5	0.010295885344429	0.014826074895978	0.016061581137309	289	180	599	21600	63	39.69	13	468.781302170284	7.81302170283806
345	400	three	GSU	Tie19	160	three	no return	9	0.370651872399445	0.111111111111111	0.041183541377716	110.9	126.2	1.377	95.6	0.010295885344429	0.014826074895978	0.016061581137309	289	140	599	21600	35	22.05	16	576.961602671119	9.61602671118531
345	405	single	GSU	Tie20	570	two	two flux return	9	0.065409153952843	0.142857142857143	0.009344164850406	101.3	126.6	2.277	76	0.002336041212602	0.003363899346146	0.003644224291658	289	140	599	21600	54	34.02	14	504.841402337229	8.41402337228715
345	405	three	TRA	Tie21	450	three	two flux return	9	0.370651872399445	0.111111111111111	0.041183541377716	92.2	108.3	1.449	76.1	0.010295885344429	0.014826074895978	0.016061581137309	289	120	599	21600	41	25.83	13	468.781302170284	7.81302170283806
345	400	three	GSU	Tie22	310	three	two flux return	9	0.370651872399445	0.111111111111111	0.041183541377716	119.7	139.9	1.818	99.5	0.010295885344429	0.014826074895978	0.016061581137309	289	160	599	21600	40	25.2	14	504.841402337229	8.41402337228715
345	420	three	GSU	Tie23	910	three	two flux return	9	0.370651872399445	0.111111111111111	0.041183541377716	118	146.6	2.574	89.4	0.010295885344429	0.014826074895978	0.016061581137309	289	160	599	21600	54	34.02	15	540.901502504174	9.01502504173623
345	335	single	Auto	Tie24	100	one	two flux return	9	0.065409153952843	0.142857142857143	0.009344164850406	230	296.6	5.994	163.4	0.002336041212602	0.003363899346146	0.003644224291658	289	350	599	21600	59	37.17	13	468.781302170284	7.81302170283806
345	345	single	Auto	Tie25	133.33	one	two flux return	9	0.065409153952843	0.142857142857143	0.009344164850406	206.2	259.9	4.833	152.5	0.002336041212602	0.003363899346146	0.003644224291658	289	300	599	21600	54	34.02	14	504.841402337229	8.41402337228715
230	275	three	TRA	Tie26	120	three	no return	9	0.28876560332871	0.142857142857143	0.041252229046959	122.2	151.8	2.664	92.6	0.01031305726174	0.014850802456905	0.016088369328314	289	160	599	21600	56	35.28	13	468.781302170284	7.81302170283806
230	275	three	Auto	Tie27	500	three	no return	9	0.28876560332871	0.142857142857143	0.041252229046959	122.8	156.7	3.051	88.9	0.01031305726174	0.014850802456905	0.016088369328314	289	180	599	21600	57	35.91	13	468.781302170284	7.81302170283806
345	330	three	Auto	Tie28	200	three	no return	9	0.370651872399445	0.111111111111111	0.041183541377716	158.5	209.3	4.572	107.7	0.010295885344429	0.014826074895978	0.016061581137309	289	250	599	21600	62	39.06	12	432.721202003339	7.21202003338898
345	345	single	GSU	Tie29	500	two	two flux return	9	0.065409153952843	0.142857142857143	0.009344164850406	100.9	128.8	2.511	73	0.002336041212602	0.003363899346146	0.003644224291658	289	140	599	21600	61	38.43	13	468.781302170284	7.81302170283806
345	345	three	Auto	Tie30	500	three	two flux return	9	0.370651872399445	0.111111111111111	0.041183541377716	146.1	182	3.231	110.2	0.010295885344429	0.014826074895978	0.016061581137309	289	200	599	21600	55	34.65	13	468.781302170284	7.81302170283806
345	345	three	Auto	Tie31	800	three	two flux return	9	0.370651872399445	0.111111111111111	0.041183541377716	134.1	167.9	3.042	100.3	0.010295885344429	0.014826074895978	0.016061581137309	289	180	599	21600	57	35.91	13	468.781302170284	7.81302170283806
345	345	three	GSU	Tie32	315	three	two flux return	9	0.370651872399445	0.111111111111111	0.041183541377716	132.7	168.8	3.249	96.6	0.010295885344429	0.014826074895978	0.016061581137309	289	180	599	21600	60	37.8	13	468.781302170284	7.81302170283806
230	230	single	Auto	Tie33	133.33	one	two flux return	9	0.09625520110957	0.2	0.019251040221914	165.7	213.4	4.293	118	0.004812760055479	0.006930374479889	0.007507905686546	289	250	599	21600	57	35.91	13	468.781302170284	7.81302170283806
230	231	single	Auto	Tie34	66.6	one	two flux return	9	0.09625520110957	0.2	0.019251040221914	162.2	204.4	3.798	120	0.004812760055479	0.006930374479889	0.007507905686546	289	250	599	21600	52	32.76	14	504.841402337229	8.41402337228715
230	230	single	GSU	Tie35	100	two	no return	9	0.09625520110957	0.2	0.019251040221914	125.5	145.8	1.827	105.2	0.004812760055479	0.006930374479889	0.007507905686546	289	160	599	21600	39	24.57	13	468.781302170284	7.81302170283806
230	230	three	Auto	Tie36	160	three	no return	9	0.28876560332871	0.142857142857143	0.041252229046959	196.4	256.5	5.409	136.3	0.01031305726174	0.014850802456905	0.016088369328314	289	300	599	21600	61	38.43	13	468.781302170284	7.81302170283806
230	230	three	GSU	Tie37	290	three	no return	9	0.28876560332871	0.142857142857143	0.041252229046959	80	135	4.95	25	0.01031305726174	0.014850802456905	0.016088369328314	289	160	599	21600	101	63.63	13	468.781302170284	7.81302170283806
230	230	three	Auto	Tie38	420	three	no return	9	0.28876560332871	0.142857142857143	0.041252229046959	102.5	144.3	3.762	60.7	0.01031305726174	0.014850802456905	0.016088369328314	289	160	599	21600	79	49.77	14	504.841402337229	8.41402337228715
230	242	single	GSU	Tie39	300	two	two flux return	9	0.09625520110957	0.2	0.019251040221914	101.6	127.8	2.358	75.4	0.004812760055479	0.006930374479889	0.007507905686546	289	140	599	21600	57	35.91	14	504.841402337229	8.41402337228715
230	240	single	GSU	Tie40	466	two	two flux return	9	0.09625520110957	0.2	0.019251040221914	65.8	101.4	3.204	30.2	0.004812760055479	0.006930374479889	0.007507905686546	289	120	599	21600	88	55.44	13	468.781302170284	7.81302170283806
230	225	three	GSU	Tie41	240	three	two flux return	9	0.28876560332871	0.142857142857143	0.041252229046959	108	127.5	1.755	88.5	0.01031305726174	0.014850802456905	0.016088369328314	289	140	599	21600	43	27.09	14	504.841402337229	8.41402337228715
in range(0,len(thermaldata[1])):	230	three	Auto	Tie42	560	three	two flux return	9	0.28876560332871	0.142857142857143	0.041252229046959	111.6	139.4	2.502	83.8	0.01031305726174	0.014850802456905	0.016088369328314	289	160	599	21600	53	33.39	13	468.781302170284	7.81302170283806

## Voltage and Phase Fractional Populations
Voltage Class	Approximate Number in US Grid	Fractional Transformer Population	Phase	Fractional Population by phase	Net Fractional Population
230kV	1388	0.38502080443828	Single	0.25	0.09625520110957
230kV	1388	0.38502080443828	Three	0.75	0.28876560332871
345kV	1572	0.436061026352289	Single	0.15	0.065409153952843
345kV	1572	0.436061026352289	Three	0.85	0.370651872399445
500kV	587	0.162829403606103	Single	0.66	0.107467406380028
500kV	587	0.162829403606103	Three	0.34	0.055361997226075
765kV	58	0.016088765603329	Single	0.97	0.015606102635229
765kV	58	0.016088765603329	Three	0.03	0.0004826629681
				Should be 1:	1

## GIC per Phase per Unit Field
Voltage Class	Average Power Line Length (km)	Estimated GIC per Phase Per Unit E field (A/(V/km))
69kV	23.2
115kV	23.04
230kV	54.4	9
345kV	58.4	9
500kV	86.56	37
735kV	103.52	34