## Thermal
Approximate Voltage Class	Voltage Rating	phase	Type	Name	MVA	wound limb	return	Estimated GIC per Phase Per Unit E field (A/(V/km))	Estimated Fractional Population of the voltage and phase class	Assumed Fractional Population For this voltage class and phase	This transformer type fractional population	Asymptotic Temp rise at 0 A GIC ( design 2)	Asymptotic Temp rise at 10 A GIC (design 2)	Asymptotic Temp rise at 20 A GIC (design 2)	Asymptotic Temp rise at 40 A GIC (design 2)	Asymptotic Temp rise at 50 A GIC (design 2)	Asymptotic Temp rise at 100 A GIC ( design 2)	Asymptotic Temp rise at 200 A GIC (design 2)	This transformer age 25-40 (25% of transformers, 160C short term limit) Fractional Population	This transformer age 0-25 (36% of transformers, 180C short term limit) Fractional Population	This transformer age >40 (39% of transformers, 140C short term limit) Fractional Population	height y axis (pixels)	Temp range y axis (K)	width x axis (pixels)	Time range x axis (seconds)	Height 100C to 200C (pixels)	63% of height (px)	pixels along x for 63% height	time constant (s)	time constant (m)
voltageClass	voltage	phase		name				GICperE	voltagePhasePercent			temprise0	temprise10	temprise20	temprise40	temprise50	temprise100	temprise200	pop25to40	pop0to25	pop40plus								tau
500	526	single	GSU	Tie1	92	one	two flux return	37	0.107467406380028	0.142857142857143	0.015352486625718	0	62.6	101	128.7	134.5	150.4	167.2	0.00383812165643	0.005526895185259	0.00598746978403	289	180	599	21600	29	18.27	14	504.841402337229	8.41402337228715
500	525	single	Auto	Tie2	374	one	two flux return	37	0.107467406380028	0.142857142857143	0.015352486625718	0	37.3	71.1	110.3	121	152.4	187.3	0.00383812165643	0.005526895185259	0.00598746978403	289	200	599	21600	54	34.02	14	504.841402337229	8.41402337228715
500	525	single	Auto	Tie3	500	two	no return	37	0.107467406380028	0.142857142857143	0.015352486625718	0	28.5	60.2	98.5	110.6	140.1	175.8	0.00383812165643	0.005526895185259	0.00598746978403	289	200	599	21600	48	30.24	11	396.661101836394	6.6110183639399
500	525	three	Auto	Tie4	300	three	no return	37	0.055361997226075	0.25	0.013840499306519	0	0.5	30.7	110	127.9	171.6	220.5	0.00346012482663	0.004982579750347	0.005397794729542	289	250	599	21600	48	30.24	9	324.540901502504	5.40901502504174
500	525	three	Auto	Tie5	560	three	no return	37	0.055361997226075	0.25	0.013840499306519	0	0.8	37.1	109.9	127.8	172.3	238	0.00346012482663	0.004982579750347	0.005397794729542	289	250	599	21600	79	49.77	14	504.841402337229	8.41402337228715
500	500	single	Auto	Tie6	292	two	two flux return	37	0.107467406380028	0.142857142857143	0.015352486625718	0	32.1	65.7	103.7	114	141.5	168.2	0.00383812165643	0.005526895185259	0.00598746978403	289	180	599	21600	45	28.35	13	468.781302170284	7.81302170283806
500	500	single	Auto	Tie7	672	two	two flux return	37	0.107467406380028	0.142857142857143	0.015352486625718	0	17.8	37.6	72	84.7	120.9	153.7	0.00383812165643	0.005526895185259	0.00598746978403	289	180	599	21600	54	34.02	12	432.721202003339	7.21202003338898
500	525	single	Auto	Tie8	460	two	two flux return	37	0.107467406380028	0.142857142857143	0.015352486625718	0	27.8	54.1	90.9	103.7	133.2	167.1	0.00383812165643	0.005526895185259	0.00598746978403	289	180	599	21600	56	35.28	13	468.781302170284	7.81302170283806
500	500	three	Auto	Tie9	840	three	two flux return	37	0.055361997226075	0.25	0.013840499306519	0	41.6	77.1	115.3	125.2	157.8	193.7	0.00346012482663	0.004982579750347	0.005397794729542	289	250	599	21600	43	27.09	13	468.781302170284	7.81302170283806
500	525	three	GSU	Tie10	300	three	two flux return	37	0.055361997226075	0.25	0.013840499306519	0	36.8	65.9	103.5	115.9	142.2	161.4	0.00346012482663	0.004982579750347	0.005397794729542	289	180	599	21600	32	20.16	12	432.721202003339	7.21202003338898
735	735	single	GSU	Tie11	100	two	no return	34	0.015606102635229	0.333333333333333	0.005202034211743	0	56.8	92.6	126.5	133.7	153.9	174.6	0.001300508552936	0.001872732316227	0.00202879334258	315	200	645	21600	36	22.68	16	535.813953488372	8.93023255813954
735	765	single	Auto	Tie12	373.33	two	two flux return	34	0.015606102635229	0.333333333333333	0.005202034211743	0	52.3	89	120	130.3	160.5	194.8	0.001300508552936	0.001872732316227	0.00202879334258	315	250	645	21600	47	29.61	15	502.325581395349	8.37209302325581
735	746	single	Auto	Tie13	750	two	two flux return	34	0.015606102635229	0.333333333333333	0.005202034211743	0	30.6	61.6	100.1	112.2	142.9	179.6	0.001300508552936	0.001872732316227	0.00202879334258	315	200	645	21600	62	39.06	16	535.813953488372	8.93023255813954
345	400	single	Auto	Tie14	167	one	two flux return	9	0.065409153952843	0.142857142857143	0.009344164850406	0	59.1	88.5	106.4	112.9	134.2	154.9	0.002336041212602	0.003363899346146	0.003644224291658	289	180	599	21600	36	22.68	15	540.901502504174	9.01502504173623
345	420	single	Auto	Tie15	360	one	two flux return	9	0.065409153952843	0.142857142857143	0.009344164850406	0	45.6	81.1	108.6	113.7	135.5	163.4	0.002336041212602	0.003363899346146	0.003644224291658	289	180	599	21600	47	29.61	13	468.781302170284	7.81302170283806
500	433	single	GSU	Tie16	121.33	two	no return	37	0.107467406380028	0.142857142857143	0.015352486625718	0	29.9	55.7	90.5	102	127.8	150.4	0.00383812165643	0.005526895185259	0.00598746978403	289	160	599	21600	43	27.09	13	468.781302170284	7.81302170283806
345	410	single	GSU	Tie17	94	two	no return	9	0.065409153952843	0.142857142857143	0.009344164850406	0	42.2	71	103	109.9	128.4	146.8	0.002336041212602	0.003363899346146	0.003644224291658	289	160	599	21600	36	22.68	14	504.841402337229	8.41402337228715
345	420	three	Auto	Tie18	750	three	no return	9	0.370651872399445	0.111111111111111	0.041183541377716	0	0	0.1	21.1	49.6	116.8	154.1	0.010295885344429	0.014826074895978	0.016061581137309	289	180	599	21600	63	39.69	13	468.781302170284	7.81302170283806
345	400	three	GSU	Tie19	160	three	no return	9	0.370651872399445	0.111111111111111	0.041183541377716	0	0.1	8.6	75.1	90.4	110.9	126.2	0.010295885344429	0.014826074895978	0.016061581137309	289	140	599	21600	35	22.05	16	576.961602671119	9.61602671118531
345	405	single	GSU	Tie20	570	two	two flux return	9	0.065409153952843	0.142857142857143	0.009344164850406	0	13.2	27.2	56.8	68.2	101.3	126.6	0.002336041212602	0.003363899346146	0.003644224291658	289	140	599	21600	54	34.02	14	504.841402337229	8.41402337228715
345	405	three	TRA	Tie21	450	three	two flux return	9	0.370651872399445	0.111111111111111	0.041183541377716	0	17.4	33.4	56	64.7	92.2	108.3	0.010295885344429	0.014826074895978	0.016061581137309	289	120	599	21600	41	25.83	13	468.781302170284	7.81302170283806
345	400	three	GSU	Tie22	310	three	two flux return	9	0.370651872399445	0.111111111111111	0.041183541377716	0	24.8	49	81	92.2	119.7	139.9	0.010295885344429	0.014826074895978	0.016061581137309	289	160	599	21600	40	25.2	14	504.841402337229	8.41402337228715
345	420	three	GSU	Tie23	910	three	two flux return	9	0.370651872399445	0.111111111111111	0.041183541377716	0	20.2	40.5	74.6	86.1	118	146.6	0.010295885344429	0.014826074895978	0.016061581137309	289	160	599	21600	54	34.02	15	540.901502504174	9.01502504173623
345	335	single	Auto	Tie24	100	one	two flux return	9	0.065409153952843	0.142857142857143	0.009344164850406	0	110.5	140.5	173.5	188	230	296.6	0.002336041212602	0.003363899346146	0.003644224291658	289	350	599	21600	59	37.17	13	468.781302170284	7.81302170283806
345	345	single	Auto	Tie25	133.33	one	two flux return	9	0.065409153952843	0.142857142857143	0.009344164850406	0	93.5	127	154	166.8	206.2	259.9	0.002336041212602	0.003363899346146	0.003644224291658	289	300	599	21600	54	34.02	14	504.841402337229	8.41402337228715
230	275	three	TRA	Tie26	120	three	no return	9	0.28876560332871	0.142857142857143	0.041252229046959	0	0	4.3	74.3	91.7	122.2	151.8	0.01031305726174	0.014850802456905	0.016088369328314	289	160	599	21600	56	35.28	13	468.781302170284	7.81302170283806
230	275	three	Auto	Tie27	500	three	no return	9	0.28876560332871	0.142857142857143	0.041252229046959	0	0.1	13.2	66.5	86.4	122.8	156.7	0.01031305726174	0.014850802456905	0.016088369328314	289	180	599	21600	57	35.91	13	468.781302170284	7.81302170283806
345	330	three	Auto	Tie28	200	three	no return	9	0.370651872399445	0.111111111111111	0.041183541377716	0	2.2	53.1	108.8	118.9	158.5	209.3	0.010295885344429	0.014826074895978	0.016061581137309	289	250	599	21600	62	39.06	12	432.721202003339	7.21202003338898
345	345	single	GSU	Tie29	500	two	two flux return	9	0.065409153952843	0.142857142857143	0.009344164850406	0	11.4	24.8	52.9	64.7	100.9	128.8	0.002336041212602	0.003363899346146	0.003644224291658	289	140	599	21600	61	38.43	13	468.781302170284	7.81302170283806
345	345	three	Auto	Tie30	500	three	two flux return	9	0.370651872399445	0.111111111111111	0.041183541377716	0	31.8	64	103.1	115.6	146.1	182	0.010295885344429	0.014826074895978	0.016061581137309	289	200	599	21600	55	34.65	13	468.781302170284	7.81302170283806
345	345	three	Auto	Tie31	800	three	two flux return	9	0.370651872399445	0.111111111111111	0.041183541377716	0	22.8	47.4	85.6	98.1	134.1	167.9	0.010295885344429	0.014826074895978	0.016061581137309	289	180	599	21600	57	35.91	13	468.781302170284	7.81302170283806
345	345	three	GSU	Tie32	315	three	two flux return	9	0.370651872399445	0.111111111111111	0.041183541377716	0	20.3	42.4	81.2	94.1	132.7	168.8	0.010295885344429	0.014826074895978	0.016061581137309	289	180	599	21600	60	37.8	13	468.781302170284	7.81302170283806
230	230	single	Auto	Tie33	133.33	one	two flux return	9	0.09625520110957	0.2	0.019251040221914	0	43.6	80.6	121.5	130.8	165.7	213.4	0.004812760055479	0.006930374479889	0.007507905686546	289	250	599	21600	57	35.91	13	468.781302170284	7.81302170283806
230	231	single	Auto	Tie34	66.6	one	two flux return	9	0.09625520110957	0.2	0.019251040221914	0	55.6	95.8	125.5	133.1	162.2	204.4	0.004812760055479	0.006930374479889	0.007507905686546	289	250	599	21600	52	32.76	14	504.841402337229	8.41402337228715
230	230	single	GSU	Tie35	100	two	no return	9	0.09625520110957	0.2	0.019251040221914	0	27	52.5	88	99.7	125.5	145.8	0.004812760055479	0.006930374479889	0.007507905686546	289	160	599	21600	39	24.57	13	468.781302170284	7.81302170283806
230	230	three	Auto	Tie36	160	three	no return	9	0.28876560332871	0.142857142857143	0.041252229046959	0	28.8	91.3	138.8	154.4	196.4	256.5	0.01031305726174	0.014850802456905	0.016088369328314	289	300	599	21600	61	38.43	13	468.781302170284	7.81302170283806
230	230	three	GSU	Tie37	290	three	no return	9	0.28876560332871	0.142857142857143	0.041252229046959	0	0	0.1	4.5	15.4	80	135	0.01031305726174	0.014850802456905	0.016088369328314	289	160	599	21600	101	63.63	13	468.781302170284	7.81302170283806
230	230	three	Auto	Tie38	420	three	no return	9	0.28876560332871	0.142857142857143	0.041252229046959	0	0	0	3	19.1	102.5	144.3	0.01031305726174	0.014850802456905	0.016088369328314	289	160	599	21600	79	49.77	14	504.841402337229	8.41402337228715
230	242	single	GSU	Tie39	300	two	two flux return	9	0.09625520110957	0.2	0.019251040221914	0	14.9	31.4	56.4	66.2	101.6	127.8	0.004812760055479	0.006930374479889	0.007507905686546	289	140	599	21600	57	35.91	14	504.841402337229	8.41402337228715
230	240	single	GSU	Tie40	466	two	two flux return	9	0.09625520110957	0.2	0.019251040221914	0	3.3	13.4	30.2	37.6	65.8	101.4	0.004812760055479	0.006930374479889	0.007507905686546	289	120	599	21600	88	55.44	13	468.781302170284	7.81302170283806
230	225	three	GSU	Tie41	240	three	two flux return	9	0.28876560332871	0.142857142857143	0.041252229046959	0	18	37.8	66.7	76.9	108	127.5	0.01031305726174	0.014850802456905	0.016088369328314	289	140	599	21600	43	27.09	14	504.841402337229	8.41402337228715
230	230	three	Auto	Tie42	560	three	two flux return	9	0.28876560332871	0.142857142857143	0.041252229046959	0	14.5	30.1	64.7	77	111.6	139.4	0.01031305726174	0.014850802456905	0.016088369328314	289	160	599	21600	53	33.39	13	468.781302170284	7.81302170283806

## Voltage and Phase Fractional Populations
Voltage Class	Approximate Number in US Grid	Fractional Transformer Population	Phase	Fractional Population by phase	Net Fractional Population		Assume 33% spares for single phase, 15% overall	fractional population	percent spares of total population
230kV	1388	0.38502080443828	Single	0.25	0.09625520110957		single	0.28473786407767	0.094912621359223
230kV	1388	0.38502080443828	Three	0.75	0.28876560332871		three	0.71526213592233	0.055087378640777	← Overall spares for 3 phase
345kV	1572	0.436061026352289	Single	0.15	0.065409153952843			1	0.15
345kV	1572	0.436061026352289	Three	0.85	0.370651872399445
500kV	587	0.162829403606103	Single	0.66	0.107467406380028
500kV	587	0.162829403606103	Three	0.34	0.055361997226075
765kV	58	0.016088765603329	Single	0.97	0.015606102635229
765kV	58	0.016088765603329	Three	0.03	0.0004826629681
				Should be 1:	1

## GIC per Phase per Unit Field
Voltage Class	Average Power Line Length (km)	Estimated GIC per Phase Per Unit E field (A/(V/km))
69kV	23.2
115kV	23.04
230kV	54.4	9
345kV	58.4	9
500kV	86.56	37
735kV	103.52	34

## Steady State Temps
Current
	Tie1	Tie2	Tie3	Tie4	Tie5	Tie6	Tie7	Tie8	Tie9	Tie10	Tie11	Tie12	Tie13	Tie14	Tie15	Tie16	Tie17	Tie18	Tie19	Tie20	Tie21	Tie22	Tie23	Tie24	Tie25	Tie26	Tie27	Tie28	Tie29	Tie30	Tie31	Tie32	Tie33	Tie34	Tie35	Tie36	Tie37	Tie38	Tie39	Tie40	Tie41	Tie42
0	0	0	0	0	0	0	0	0	0
10	62.6	37.3	28.5	0.5	0.8	32.1	17.8	27.8	41.6	36.8	56.8	52.3	30.6	59.1	45.6	29.9	42.2	0	0.1	13.2	17.4	24.8	20.2	110.5	93.5	0	0.1	2.2	11.4	31.8	22.8	20.3	43.6	55.6	27	28.8	0	0	14.9	3.3	18	14.5
20	101	71.1	60.2	30.7	37.1	65.7	37.6	54.1	77.1	65.9	92.6	89	61.6	88.5	81.1	55.7	71	0.1	8.6	27.2	33.4	49	40.5	140.5	127	4.3	13.2	53.1	24.8	64	47.4	42.4	80.6	95.8	52.5	91.3	0.1	0	31.4	13.4	37.8	30.1
40	128.7	110.3	98.5	110	109.9	103.7	72	90.9	115.3	103.5	126.5	120	100.1	106.4	108.6	90.5	103	21.1	75.1	56.8	56	81	74.6	173.5	154	74.3	66.5	108.8	52.9	103.1	85.6	81.2	121.5	125.5	88	138.8	4.5	3	56.4	30.2	66.7	64.7
50	134.5	121	110.6	127.9	127.8	114	84.7	103.7	125.2	115.9	133.7	130.3	112.2	112.9	113.7	102	109.9	49.6	90.4	68.2	64.7	92.2	86.1	188	166.8	91.7	86.4	118.9	64.7	115.6	98.1	94.1	130.8	133.1	99.7	154.4	15.4	19.1	66.2	37.6	76.9	77
100	150.4	152.4	140.1	171.6	172.3	141.5	120.9	133.2	157.8	142.2	153.9	160.5	142.9	134.2	135.5	127.8	128.4	116.8	110.9	101.3	92.2	119.7	118	230	206.2	122.2	122.8	158.5	100.9	146.1	134.1	132.7	165.7	162.2	125.5	196.4	80	102.5	101.6	65.8	108	111.6
200	167.2	187.3	175.8	220.5	238	168.2	153.7	167.1	193.7	161.4	174.6	194.8	179.6	154.9	163.4	150.4	146.8	154.1	126.2	126.6	108.3	139.9	146.6	296.6	259.9	151.8	156.7	209.3	128.8	182	167.9	168.8	213.4	204.4	145.8	256.5	135	144.3	127.8	101.4	127.5	139.4